## Grand Summary_Edaga Hamus PS
BILLS OF QUANTITIES
Project: REHABILITATION AND RECONSTRUCTION OF SCHOOL WASH FACILITIES IN TIGRAY REGION
School Name:Edaga Hamus PRIMARY SCHOOL
Location: Edaga Hamus woreda_Estern Zone of Tigray Region
Item no. | Infrastructure Name | Amount [ETB]
1 | Reservoir establishment | 0
2 | Water Point 1 | 0
3 | Toilet 1 | 0
| Grnad Total [ETB] | 0

## Detailed BOQ_Edaga Hamus PS
BILLS OF QUANTITIES
Project: REHABILITATION AND RECONSTRUCTION OF SCHOOL WASH FACILITIES IN TIGRAY REGION
School Name: Edaga Hamus PRIMARY SCHOOL
Location: Edaga Hamus woreda_Estern Zone of Tigray Region
ITEM | DESCRIPTION | UNIT | QTY | RATE(ETB) | AMOUNT(ETB)
GENERAL
The activities listed below are for the rehabilitation and reconstruction of the WASH facilities in the school and include improving existing structures through renewal, restoration, maintenance, refitting, modification, and the installation of new materials to replace damaged or outdated components; for each activity, the contractor shall include all necessary associated works, whether explicitly stated or not, including removal of damaged materials, demolition, carting away debris, making good, and reinstatement, to ensure proper and complete execution of the works to the satisfaction and approval of the Engineer.
1. Reservoir establishment [ STAND + WATER TANKER]
SEAT FOR A WATER TANKER [ 10,000 LITRES]
1. Excavation and earth works
1.1 | Clear and remove top soil to an average depth of 20 cm | M2 | 13.44 |  | 0
1.2 | Bulk excavation in ordinary soil to a depth not exceeding 80cm | M3 | 10.752 |  | 0
1.3 | Trench excavation in ordinary soil to a depth notexceeding 150 cm from reduced ground level. | M3 | 8.48 |  | 0
1.4 | Back fill around foundation with brought material from quarry waste and compact in layers not exceeding 20 cm thick. | M3 | 10.752 |  | 0
1.5 | 25 cm thick basaltic stone hardcore well rolled,consolidated and blinded with crushed stone . | M2 | 13.44 |  | 0
| TOTAL CARRIED TO SUMMARY |  |  |  | 0
2. Concrete works
2.1 | 5 cm lean concrete quality C-5, 150 kg of cement/m3, under
| a) Masonry | M2 | 13.44 |  | 0
| b) C-25 mass concrete 15cm thick | M2 | 13.44 |  | 0
2.2 | Provide, cut and fix in position sawn zigba wood or - steel formwork to, |  |  | 0 | 0
| a) For TOP Slab | M2 | 2.22 |  | 0
2.3 | Mild steel reinforcement according to structural - drawings. Price includes cutting, bending, placing in position and tying wire |  |  | 0 | 0
| a) Dia 8 mm deformed bara | kg | 69.88 |  | 0
| TOTAL CARRIED TO SUMMARY |  |  |  | 0
3. Massonry works
3.1 | 50 cm thick hard trachite stone bedded in cement mortar (1:3).Price shall include mortar bed.
| a) Below ground level | M3 | 11.84 |  | 0
| a) Above ground level | M3 | 22.2 |  | 0
3.2 | Apply Two coats of plastering in cement mortar (1:3) . Price shall include pre-cleaning and preparation of the surface . | M2 | 22.2 |  | 0
| TOTAL CARRIED TO SUMMARY |  |  |  | 0
4. FIBER GLASS WATER TANK (10,000 LITRES)
4.1 | Supply, deliver, and install approved 10,000 litres capacity Fiber Glass Reinforced Plastic (FRP) water tank, complete in all respects, in accordance with the drawings and sanitary site plan. The tank shall be manufactured from high-quality FRP material with a minimum wall thickness of 5 mm, resistant to corrosion, UV radiation, and suitable for potable water storage. The tank shall be structurally sound, watertight, and free from defects. The work shall include all necessary accessories, fittings, and connections, including but not limited to: Inlet pipe complete with gate valve, Outlet pipe complete with gate valve,Drain pipe complete with gate valve,Overflow pipe with proper discharge arrangement Vent pipe with insect-proof vent cap, Manhole opening complete with heavy-duty, lockable, and easily removable cover (lid) located above the inlet pipe The tank shall be properly positioned, aligned, and fixed on a prepared base/seat (concrete or steel support) capable of safely carrying the full load of the tank when filled. All pipe connections shall be watertight and properly sealed, and the installation shall include all necessary jointing materials, supports, brackets, and anchoring bolts. The contractor shall test the tank for leakage, clean internally, and disinfect before commissioning. Complete with:All fittings and valves, Base/seat preparation and fixing Connection to inlet, outlet, overflow, and drainage system, Testing, cleaning, and commissioning. | Pcs | 1 |  | 0
4.2 | SUPPLY AND INSTALL HDPE PIPE, PN-16 Supply and install 1.57-inch (40 mm) High Density Polyethylene (HDPE) pipes, PN-16 pressure rating, for the site cold water distribution system and connection to the main grid line properly, complete with all necessary fittings, valves, jointing materials, supports, and accessories. The installation shall include proper alignment, trenching, bedding, backfilling, and jointing using electrofusion or heat fusion methods, and the system shall be tested for leaks, pressure, and correct operation before commissioning. | Ml | 120 |  | 0
| TOTAL CARRIED TO SUMMARY |  |  |  | 0
| TOTAL [ STAND +WATER TANKER] |  |  |  | 0
2. NEW CONSTRUCTION OF WATER POINT 1 & ROTO SEAT
Item No. | DESCRIPTION | Unit | Qty | Unit Price (Birr) | Total Amount (Birr)
1. Earth work ( For Water Point & Roto Seat)
1.1 | Clearing and striping of top soil to a minimum depth of 200 mm inside the fenced compound of each water point. NB : it inculdes demolishing the exisiting Water point. | m2 | 74 |  | 0
1.2 | Excavation for Water point foundation , soak away pit, ramp and valve chamber to a depth not exeeding 150cm | m3 | 34.35 |  | 0
1.3 | Back fill under hard core with selected aggregate or good dry filling material, compact well in layers not exceeding 25cm thickness. | m3 | 21.481 |  | 0
1.4 | Provide and fill hard core with hard basaltic or equivalent stone, well compacted and blinded with crushed stone | m2 | 19.42 |  | 0
1.5 | Cart away and dispose all excavated material to appropriate distance not exceeding 1 Km. | m3 | 49.15 |  | 0
| Sub Total |  |  |  | 0
2. Concrete Work ( For Water Point & Roto Seat)
2.1 | C-5 lean concrete | m2 | 20.42 |  | 0
2.2 | C-15 concrete mass concrete 10cm thick | m3 | 6.203 |  | 0
2.3 | Provide and fix formwork | m2 | 14.512 |  | 0
2.4 | Provide cut, and fix in position reinforced steel bar all according to structural drawing, Price shall include tying wires |  |  | 0 | 0
| a)Diametr 6 mm | Kg | 43.2 |  | 0
| b)Diametr 10 mm | Kg | 73.5 |  | 0
| Sub Total |  |  |  | 0
3. Masonery Work ( For Water Point & Roto Seat)
3.1 | Provide and construct 400mm thick trychytic masonry wall grouted and filled with (1:3) mortar for foundation and super structure | m3 | 19.2 |  | 0
3.2 | Two coat Plastering to smooth finish for waterpoint wall and surface | m2 | 27 |  | 0
3.3 | Masonery pavement around the water point as per the drawing (200 mm thick with 1:3 mortar) | m2 | 4.45 |  | 0
| Sub Total |  |  |  | 0
4. Pipework
4.1 Supplying and installing GS pipes
4.1.1 | DN 40 GS | ml | 18 |  | 0
4.1.2 | DN20 GS | ml | 12 |  | 0
| 4.2 Supplying and fixing fittings |  |  | 0 | 0
4.2.1 | Cross tee DN 40 | No | 2 |  | 0
4.2.2 | Reducer 40x20 | No | 12 |  | 0
4.2.3 | Tee DN 40 | No | 6 |  | 0
4.2.4 | DN 40 Bend (elbow) 90 degree | No | 4 |  | 0
4.2.5 | Faucet DN 20 | No | 12 |  | 0
4.2.6 | Socket DN 20 | No | 12 |  | 0
4.2.7 | Gate valve DN 40 | No | 1 |  | 0
4.2.8 | Union DN 40 | No | 1 |  | 0
4.2.9 | Nipples DN 40 | No | 2 |  | 0
4.2.10 | Water meter DN 40 | No | 1 |  | 0
4.3 | Construct two valve chambers for water meter and gate valve , covered with 700*700*6mm sheet metal with latch and lock as per the drawing | Pcs | 1 |  | 0
| Sub Total |  |  |  | 0
5. Drainage
5.1 | Reinforced Concrete drainage ditch from water point to soak away pitas per the drawing, Price including excavation and any other incedental works | ml | 17 |  | 0
5.2 | Supply and place boulders, crashed agregate and sand to form the soak away as per the drawing | m3 | 1.5 |  | 0
5.3 | Supplying and installing GS pipes 1 1/2 " | ml | 90 |  | 0
5.5 | FENCING (6.2 m × 6.2 m) FOR WATER POINT – Supply and install a a wire mesh chain link fence around the water point using durable angle iron poles (40 mm × 40 mm) spaced at 1.2 m intervals. The fence shall be completed with suitable chain link mesh and include a lockable access door fabricated from flat metal sheet of 1.2 mm thickness for secure entry. All materials shall be properly painted or treated to resist corrosion, and the fence shall be firmly anchored into the ground to ensure stability and safety. The installation shall provide controlled access, prevent unauthorized entry, and maintain hygiene around the water point, while allowing safe operation and maintenance. | Lum | 1 |  | 0
5.5
| Sub Total |  |  |  | 0
| Total |  |  |  | 0
3. MODIFICATION OF (12 SEATS) LATRINE
ITEM | DESCRIPTION | UNIT | Quantity | Unit Rate | Amount
A. SUB-STRUCTURE
1.EXCAVATION & EARTHWORKS
| General – Carefully demolish the existing partition for the 12-seat latrine in a safe and controlled manner, ensuring proper protection of surrounding structures and environment, and cart away all demolished materials to a location designated by the school within a distance not exceeding 2 km. The contractor shall clear, clean, and level the site after demolition, and carry out the work in accordance with good construction practices and safety standards. | lum | 1 |  | 0
| 2. BLOCK WORKS |  |  | 0
2.1 | 20cm thick hollow concrete block (class B) wall bedded in cement mortar 1:3 internal and external walls left for plastering. The quality has to be approved by the client prior to supply of HCB. | m2 | 101.92 |  | 0
2.2 | Ditto but 15cm thick HCB wall (class B), The quality has to be approved by the client prior to supply of HCB. | m2 | 20.8 |  | 0
| Sub Total |  |  | 0 | 0
| 3. ROOFING |  |  | 0
3.1 | Supply and fix G-30 galvanized corrugated steel sheet roofing fixed to 5x7 cm purlins at c/c 90 cm. Horizontal projection of roof area shall be taken for measurement. | m2 | 55.5 |  | 0
3.2 | Truss members of eucalyptus shall be well seasoned, straight and free of harmful defects. Each truss joint and members shall be firmly connected with strips of band iron. Price shall include approved 2 coats of anti termite paint to truss and purlins. Truss should be fixed with the top tie beam with Ø6 rebar and spaced at 120cm from each other. |  |  | 0
| a) Ø 10 cm or above eucalyptus for all members | ml | 172 |  | 0
| b) 5x7 cm zigba purlins , Price includes anti termite treatment | ml | 75 |  | 0
3.3 | Supply and fix 20x2.5cm kerero or equivalent fascia board including 3 coats of weather resistant paint. | ml | 49.6 |  | 0
3.4 | Supply and fix 18cmx18cmx12cm gutter made of G-28 sheet metal. Provide at least 0.2% slope towards the out let and connect the gutter in position using clamp and gutter support at 1m spacing. The work includes fixing the gutter on poisiton with binding wire, fixing the wire mesh over the gutter and all necessary works thereto. Price shall include one coat anti rust and two coats synthetic paint. (Optional) | ml | 14 |  | 0
3.5 | Supply and fix Ø 110mm PVC down pipe and connect the down pipe to the water tanker. Cost includes all necessary works including fixing it with the wall, providing elbow, clamps, fischers and any other works required thereto. | ml | 24 |  | 0
| Sub Total |  |  | 0 | 0
| 4. METAL WORKS |  |  | 0
| All metal doors and windows shall be fabricated from locally manufactured frame 1.25mm thick LTZ 38mm width, pressed metal with the necessary iron mongory, accessories and three coats of paint. The doors must be fixed with simple lock inside and outside. Price includes one coat anti rust and two coats synthetic paint internally and externally. It also includes provision of 40cm plastic cover at the bottom of each door. |  |  | 0
4.1 | Ditto but 70x30 window with weir mesh and metallic frame as shown on the drawing | m2 | 0.84 |  | 0
4.2 | Ditto but 100x210. Opening of this door is as shown on the drawing and has emergency door exit for disabilities latrine as shown on the drawing | m2 | 2.1 |  | 0
4.3 | Ditto but 70x210. Opening of this door is as shown on the drawing. | m2 | 17.64 |  | 0
| Sub Total |  |  | 0 | 0
| 5. FINISHING |  |  | 0
| Cost for Finishing works which shall include all surface pre-cleaning. Preparation and application of finishing and cleaning at the end of finishing works |  |  | 0
5.1 | Three coats of plastering in cement sand mortar of ratio 1:3 to HCB walls reinforced concrete beams & columns as per the drawing | m2 | 192.5 |  | 0
5.2 | Pointing to HCB wall and exposed masonry walls in cement sand mortar of ratio 1:3 as per the drawing | m2 | 113.54 |  | 0
5.3 | 30 mm thick cement screed floor finishing in cement sand mortar of 1:3 | m2 | 73.26 |  | 0
5.4 | Construct concrete Pavement as shown in the drawing. The price includes casting 10cm C-15 concrete, formwork, Steps construction, Chip wood expansion joint @2m C/C and Pointing on exposed parts. | m2 | 29.34 |  | 0
5.5 | Install 110mm PVC vent pipe as per the drawing. The price includes providing opening hole in the CIS for passage, minimum two bracket support with HCB wall and fixing PVC with truss support & Truss. | Pcs | 10 |  | 0
5.7 | Supply and install seat for disable as per the drawing. The seat should be suitable for using and smooth. The price includes 1" GS pipe for handrail. The price includes flusing ystem, piping and all other necessary works there to for piped latrines. | Ls. | 2 |  | 0
5.8 | supply and fix according the drawing for Ramp hand rail & balustrad made of RHS Rectangular Hollow section steel tube 40*20*2 mm for vertical rows c/c 60 cm at middel both side for horzintal 15*2.5 cm & at the top 10*5*2.5 cm wanza or equivalent timber hand rail supported by 4cm width 1.25 mm thick metal sheet price inculding two coats varnish & oil paint with the with all the accessories (drawing& material quality approved by the engineer) | m2 | 14.4 |  | 0
5.9 | Supply and Install 1,000lt water tanker as shown in the drawing to be seat on a masonry platform. Cost includes 1" pipe laying to hand wash facilities and all necessary fittings as shown in the drawing. The work also includes fixing the tanker on position with dia. 6 re-bar anchored in the concrete slab/masonry wall. | Ls | 1 |  | 0
5.10 | Supply and construct handwash basin with 4 faucet connected to the latrine wall as shown on the drawing. Price includes 1/2" faucet, Ø50mm drainage PVC pipe connected to soak away pit, 1" PPR pipe connected from elevated tanker's. The soak away pit located a minimum of 10m away from the latrine. | No | 2 |  | 0
5.12 | Provide Soak away pit as per the drawing (1.4x1.4x1.5m) filled with crushed gravel at a minimum distance of 10m from the latrine. The soak away is constructed in such away to accommodate with the slope of the drain pipe of hand washing facilities. | Ls. | 1 |  | 0
5.13 | Apply wall paint to all plastered external beams and columns surfaces or as directed by the engineer | m2 | 240 |  | 0
5.14 | Construct 2.0m wide ramp of maximum slope 7%. The price includes excavation, backfilling work, hardcore, 10cm thick concrete and dia 8cm reinforcement placed every 250mm both ways at the bottom. The spacing of the reinforcement will be changed to every 150mm in the longitudinal direction at ditch crossings and the difference in quantity will be separately measured and considered in the concrete part. | ml | 5 |  | 0
5.15 | Supply & install galvanized steel pipes for water distribution to all sanitary fixtures according to the drawing, complete with the necessary connection pieces such as bends, unions, etc. unit price shall include all the necessary assistance to the installation of works such as chiselling of walls, slabs, beam, floors, etc. & closing them with concrete or cement mortar, to normal condition; & excavation , back fiil for out side the installation shall be tested at a presure of 10kg/cm2 by the expense of the contractor.(material quality approved by the engineer) sanitary installation with 1 inch galvanized steel out side the Building | ml | 200 |  | 0
| Sub Total |  |  | 0 | 0
| 6. ELECTRICAL INSTALLATION (OPTIONAL) |  |  | 0
| Supply and install :- |  |  | 0
6.1 | Light Points |  |  | 0
| Flush mounted light points fed through PVC insulated conductors of 2x2.5mm2 inside PVC conduits of 13mm diameter, including junction boxes with covers and insulating screw cap connectors, complete | No | 12 |  | 0
6.2 | Flush Mounted Switches (Type Legrand Suno or Equivalent) |  |  | 0
| Flush mounting Two way switch, 6A - flush mounted | No | 4 |  | 0
6.3 | Light Fittings and Lamps |  |  | 0
| (Specified Type or Equivalent) |  |  | 0
| Connected and tested including lamps and accessories complete, all as specified or described in lighting fittings schedule and as shown on the drawings. |  |  | 0
| Supply and Fix sodium lamp Fixtures, E-40,125w holder | No |  | 0 | 0
| Supply and Fix Sodium lamp ,125w | No | 12 |  | 0
| PHILIPS TCW 215 with 1 x TL-D 360W Lamp or Equivalent | No | 1 |  | 0
| Sub Total |  |  |  | 0
| GRAND TOTAL FOR 12 Seat |  |  |  | 0